## Information
Cable Dimensioning tool SCS-S2 - for Smoke Control System damper unit
In a smoke control system with one master unit and a number of damper units with e.g. dampers there will be a voltage drop (ΔU) along the wire, which makes it necessary to add external power supplies between the damper units. The voltage drop depends on the resistance, thickness, and length of the wire and the power consumption in the damper units with connected dampers/detectors/sensors. The voltage drop (ΔU) can be maximum 10% before an external power supply must be added. To decide how many external power supplies are needed, calculations for the voltage drop (ΔU) must be made. An example is shown in the calculation sheet. It is recommended to use the Cable Dimensioning tool SCS-S2 calculation sheet to calculate specific project cable dimension requirements. See also the SCS Manual. This Cable Dimensioning tool SCS-S2, and all other SCS documentation, can be downloaded from www.regincontrols.com.
Cable Dimensioning tool SCS-S2, 2023-04-20, Rev A.

## Calculation sheet
Cable Dimensioning tool SCS-S2 - for Smoke System Damper unit - Calculation sheet | [11 empty] | Example data:
Grey cells are locked | Green fields for input |  |  |  | Note! The value cells for Voltage drop % and Distance, m turns red if the voltage drop is above 10 % or the length exceeds 300 m
Components: |  |  | Comment:
Damper unit | 2 | VA | Constant for all.
Damper actuator | 4 | VA | Set individually on each damper below, default 4VA
CU Resistance | 0.017 |  | Constant for all.
Number of wires | 2 |  | Constant for all.
Cable cross section | 1.5 | mm2 | Set individually on each damper below, default 1,5mm2
Tranformer voltage nominal | 24 | V AC | Nominal voltage at transformer
Transformer too first damper unit | Damper unit |  |  |  | Damper actuator |  |  |  |  | 1
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 24 | 0.083333 | 1 | 4 | 24 | 0.16667 | 1 | 0.25
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 200 | 1.5 | 4.5333
Cable length from Transformer to first damper unit: | 200 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 1.1333 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 4.722% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level powerup: | 22.8667 | V | [7 empty] | 1.1333 | Voltage drop V
[10 empty] | 4.722% | Voltage drop %
[10 empty] | 200 | Distance, m
Between damper unit No. 1 and No. 2 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 2
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.8667 | 0.087464 | 1 | 4 | 22.8667 | 0.17493 | 1 | 0.26239
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 20 | 1.5 | 0.45333
Cable length to here: | 20 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.11895 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.4956% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.7477 | V | [7 empty] | 1.2523 | Voltage drop V
[10 empty] | 5.218% | Voltage drop %
[10 empty] | 220 | Distance, m
Between damper unit No. 2 and No. 3 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 3
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.7477 | 0.087921 | 1 | 4 | 22.7477 | 0.17584 | 1 | 0.26376
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 10 | 1.5 | 0.22667
Cable length to here: | 10 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.059786 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.2491% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.6879 | V | [7 empty] | 1.3121 | Voltage drop V
[10 empty] | 5.467% | Voltage drop %
[10 empty] | 230 | Distance, m
Between damper unit No. 3 and No. 4 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 4
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.6879 | 0.088153 | 1 | 4 | 22.6879 | 0.17631 | 1 | 0.26446
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 10 | 1.5 | 0.22667
Cable length to here: | 10 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.059944 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.2498% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.628 | V | [7 empty] | 1.372 | Voltage drop V
[10 empty] | 5.717% | Voltage drop %
[10 empty] | 240 | Distance, m
Between damper unit No. 4 and No. 5 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 5
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.628 | 0.088386 | 1 | 4 | 22.628 | 0.17677 | 1 | 0.26516
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 10 | 1.5 | 0.22667
Cable length to here: | 10 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.060103 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.2504% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.5679 | V | [7 empty] | 1.4321 | Voltage drop V
[10 empty] | 5.967% | Voltage drop %
[10 empty] | 250 | Distance, m
Between damper unit No. 5 and No. 6 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 6
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.5679 | 0.088622 | 1 | 4 | 22.5679 | 0.17724 | 1 | 0.26586
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 10 | 1.5 | 0.22667
Cable length to here: | 10 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.060263 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.2511% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.5076 | V | [7 empty] | 1.4924 | Voltage drop V
[10 empty] | 6.218% | Voltage drop %
[10 empty] | 260 | Distance, m
Between damper unit No. 6 and No. 7 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 7
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.5076 | 0.088859 | 1 | 4 | 22.5076 | 0.17772 | 1 | 0.26658
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 10 | 1.5 | 0.22667
Cable length to here: | 10 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.060424 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.2518% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.4472 | V | [7 empty] | 1.5528 | Voltage drop V
[10 empty] | 6.47% | Voltage drop %
[10 empty] | 270 | Distance, m
Between damper unit No. 7 and No. 8 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 8
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.4472 | 0.089098 | 1 | 4 | 22.4472 | 0.1782 | 1 | 0.26729
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 20 | 1.5 | 0.45333
Cable length to here: | 20 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.12117 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.5049% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.326 | V | [7 empty] | 1.674 | Voltage drop V
[10 empty] | 6.975% | Voltage drop %
[10 empty] | 290 | Distance, m
Between damper unit No. 8 and No. 9 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 9
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.326 | 0.089582 | 1 | 4 | 22.326 | 0.17916 | 1 | 0.26874
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 10 | 1.5 | 0.22667
Cable length to here: | 10 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.060915 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.2538% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.2651 | V | [7 empty] | 1.7349 | Voltage drop V
[10 empty] | 7.229% | Voltage drop %
[10 empty] | 300 | Distance, m
Between damper unit No. 9 and No. 10 | Damper unit |  |  |  | Damper actuator |  |  |  |  | 10
| VA pr. Damper unit | V | I | QTY | VA pr. Damper actuator | V | I | QTY | Sum A:
Current load | 2 | 22.2651 | 0.089827 | 1 | 4 | 22.2651 | 0.17965 | 1 | 0.26948
| CU Resistance | wires | Cable length | mm2 | Sum RL:
RL: Total resistance in wire | 0.017 | 2 | 20 | 1.5 | 0.45333
Cable length to here: | 20 | meter | [7 empty] | Over this unit
Cable cross section | 1.5 | mm2 | [7 empty] | 0.12216 | Voltage drop V
Damper actuator VA | 4 | VA | [7 empty] | 0.509% | Voltage drop %
Damper actuator QTY (1 or 0 per damper unit) | 1 | pcs | [7 empty] | Total
Voltage level here: | 22.1429 | V | [7 empty] | 1.8571 | Voltage drop V
[10 empty] | 7.738% | Voltage drop %
[10 empty] | 320 | Distance, m